Maximum Clearance Reduction From Appliances

Type of Protection	As Wall Protector	As Ceiling Protector

a.)3 ½ ” Masonry Wall

no ventilation		33%		----

b.)1/2 ” noncombustible

insulation board over 1”

glass fiber or mineral

wool batts, no ventilation	50%		33%

c.)Minimum 24 gage sheet

metal spaced out 1”		66%		50%

d,)3 ½ masonry wall spaced

out 1”		66%		----

e.)1/2” noncombustible wall

spaced out over 1”		66%		50%

f.)Listed prefabricated system		Per manufacturer’s

Instructions

***NOTE: After reduction of listed clearances, clearances shall not be less than 12 inches to combustible walls and not less than 18 inches to combustible ceiling. See NFPA 9-6 2.1 (2000 edition)